# Type IIIa Cracking in ½CrMoV Steam Pipework Systems

S J Brett

## Innogy plc

Abstract

A mode of cracking termed Type IIIa has been found to occur at the welds of ½CrMoV pipework systems in the UK. This cracking mechanism is not as well documented as the more familiar Type IV cracking, which occurs on these and other ferritic steel systems, but is likely to increase in importance as plant ages. This paper summarises the available information about the initiation and development of Type IIIa cracks and brings up to date recent work on carbon diffusion local to welds, which is believed to play a role in the susceptibility to this form of cracking.

1 Introduction

The majority of large power generating units constructed in the UK in the 1960s and 1970s utilised BS3604 Grade 660 (½%chromium, ½%molybdenum, ¼%vanadium) steel welded with BS2493 2CrMoB (2¼%chromium, 1%molybdenum) weld metal for the high temperature pipework systems. Many of these units continue in operation today. Innogy for example currently owns and operates, or provides technical support to, approximately 11,500 MW of coal-fired plant in the UK with ½CrMoV steam systems welded with 2CrMo weld metal, operating typically at 568(C/175bar. The oldest units have now been in service for 200,000 hrs.

While the presence of vanadium carbide precipitates provides excellent creep strength, ½CrMoV steels have historically suffered from a number of welding related problems. Up until 2001 the following three principal cracking mechanisms affecting large CrMoV welds, which have been reviewed and compared elsewhere [1], had been identified:

Reheat Cracking

Type IV Cracking

Type IIIa Cracking

In contrast to the first two mechanisms, relatively little has been published about Type IIIa cracking, and the opportunity is taken here to summarise and update information provided in 1998 [2].

2 Type IIIa Cracking

2.1	Definition

The term “IIIa” arises from a modification of the classification system first introduced by Schüller et al [3]. Under this system a crack lying within the heat affected zone (HAZ) close to the weld fusion line was termed a Type III crack. This however did not distinguish between individual cracking mechanisms, allowing for confusion between reheat cracking, arising in this location early in life, and creep cracking occurring later in service. These cracking mechanisms are metallurgically distinct. Reheat cracking is associated with coarse grained microstructure and caused by the creep strain absorbed during the decay of residual welding stress exhausting low local ductility. Creep cracking in more ductile microstructure can occur later in life as a result of long range system loads. The term IIIa was adopted for this latter form of cracking.

In terms of cracking morphology, reheat cracking and Type IIIa cracking appear to exhibit directly opposite characteristics. Reheat cracking initiates and grows fastest in the coarsest grain structures and is often seen to be inhibited in fine grained structure. Type IIIa cracking in contrast initiates in fine grain structure and has been observed to arrest in coarse grained structure. Significant levels of Type IIIa cracking are confined to welds which have been made with fully refined HAZ structures.

The driving force for reheat cracking, residual welding stress, will eventually disappear in service, but the system loads giving rise to Type IIIa will not. Reheat cracking can therefore be expected to diminish in importance with time in service, whereas Type IIIa cracking can be expected to increase. In this respect Type IIIa cracking can be regarded as similar to Type IV cracking.

2.2	Cavitation and Micro-Crack Development

Type IIIa damage initiates close to the fusion line, as a distinct band of cavitation extending up to approximately 100 μm into the refined HAZ grain structure (Fig.1). Micro-cracks form within this band, each individually perpendicular to the longitudinal pipe axis, ie the direction of the pipework system stress.

Because long range system stresses will inevitably contain a bending component the maximum stress will normally be at the outer surface of the pipe. The primary site of the observed damage initiation is however just below the surface. This is because most welds will have a capping bead with the fusion line intersecting the surface at an acute angle. Micro-crack initiation is easier below the capping bead, where the fusion line is more perpendicular to the stress and therefore more favourably orientated for cavitation alignment and micro-crack formation.

2.3	Crack Growth

Micro-cracks eventually grow and link up to develop into macro-cracks, which follow the fusion line closely, while being displaced a few grains into the HAZ (Fig. 2). Type IIIa cracks appear to spend a greater proportion of their lives at smaller sizes than do Type IV cracks.

This is illustrated in Fig. 3 which compares the recorded through-wall dimensions of repaired Type IV and IIIa cracks found up to 1998 (micro-cracks are not included). Since the number of cracks found in a given size range should be inversely proportional to the time growing cracks spend in that size range, the figure provides evidence of relative growth rate through the wall for the two cracking mechanisms. In comparing Type IIIa with Type IV it can be seen that, except at the smallest size (<5% through-wall), both varieties of crack exhibit the same size profile.

A through-wall extent of 5% corresponds to ~3mm on a typical main steam butt weld and is approximately equivalent to the weld bead dimension along the fusion line. A preponderance of Type IIIa cracks at this size implies that a barrier exists to growth beyond one weld bead. At larger sizes Fig. 3 indicates that there is little discernible difference between Type IIIa and Type IV cracks. While there are more Type IV cracks than Type IIIa cracks, the distributions look very similar.

Because of the capping bead effect, Type IIIa cracks may grow to a substantial through-wall size before breaking out to the surface. Approximately two thirds of Type IIIa cracks recorded by Innogy were still subsurface when discovered, the largest of these reaching 64% through-wall extent. Again, in this respect they are similar to Type IV cracks.

2.4	Numbers of Cracks

Coal-fired plant operated by, or technically supported by, Innogy contain approximately 7600 large welds in their various ½CrMoV systems which had operated up to 2001. Weld repairs for Type IV or IIIa cracks or pre-crack damage had been carried out on ~5% of the weld population. Type IV cracks have been the more common of the two defect types, accounting for two thirds of repairs for cracks (Fig. 4). Type IIIa cracks have however gradually increased in significance with time. One reason for this is Type IIIa cracking tends to be more prevalent in plain butt welds. These welds have historically been regarded as having the least susceptibility to cracking and widespread inspections have generally been delayed until relatively later in service.

3 Causes of Type IIIa Cracking

3.1	Carbon Diffusion

Until recently little attention has been paid to the underlying metallurgical causes of Type IIIa cracking, the tacit assumption being that these were similar to the causes of Type IV cracking. There are however clear metallurgical differences between the two  failure locations. Whereas it can be argued that the Type IV zone will inevitably have low creep strength, as a result of the weld thermal cycles at the outer edge of the HAZ, this is not true of the Type IIIa zone. In the condition in which the weld enters service the HAZ immediately adjacent to the weld fusion line should have creep strength comparable to that of the weld metal, even in welds with fully grain refined HAZ structures. It is difficult to explain why any weld should fail in the Type IIIa region in preference to the Type IV region, without an additional weakening factor being present in the Type IIIa zone.

The additional factor appears to be carbon migration from the parent into the weld metal, a process which starts during post weld heat treatment and continues with operation at service temperature.

3.2	Evidence From Operating Plant

An exercise which compared the chemical analysis of ½CrMoV steam pipe samples taken some distance away from welds, with samples taken immediately adjacent to welds, showed clear evidence of lower carbon levels near the welds (Fig. 5). The same effect persisted even when samples from the same individual pipe section were compared. It was eventually concluded that the samples taken near the welds had been taken within a region affected by carbon depletion resulting from diffusion into the weld metal.

An early confirmation that welds suffering from Type IIIa cracking also exhibited carbon depletion near the fusion line [4] was followed by a demonstration that the depletion could extend well beyond the HAZ and some way into the parent pipe material [5]. The latter work showed that the maximum level of carbon in the weld metal and the minimum level of carbon in the parent were largely established by the post weld heat treatment. During subsequent ageing, while these maximum and minimum values remained relatively constant, the widths of the carbon enriched and carbon depleted zones increased with time. A typical carbon profile, in this case from an artificially aged specimen, is shown in Fig. 6.

These studies utilised a neutron microprobe to measure the carbon levels, but the scale and extent of carbon depletion was so great that the present author was subsequently able to demonstrate the effect using industrial measuring techniques (carbon by combustion followed by infra red detection of CO2). Using this particular technique measurements were confined to the depletion zone on the parent side of the interface.

Twelve welds taken out of service after various periods of operation were sectioned to provide thin slices of material for carbon analysis at increasing distance from the weld fusion line. Although the welds came from several different power stations and a wide range of ½CrMoV pipework systems, all showed a marked tendency of carbon level to decrease near the fusion line. This is illustrated for three of the welds in Fig. 7. The results are summarised in Fig. 8 where the normalised carbon level (actual carbon level measured divided by the background carbon level for that pipe) at 3mm from the fusion line is shown against the operating hours at which the welds were removed from service.

The results show that carbon movement is a general effect for welds of this type. Fig. 8 indicates that a weld operating for ~250000hrs at 568°C will lose about half its carbon level near the weld fusion line.

  - The Effect of Carbon Loss on Creep Strength

Attempts were made to investigate any consequential reduction of creep strength in the depletion zones adjacent to welds [6][7]. Samples similar in size to those taken for carbon analysis were obtained for small scale creep testing. The results were ambiguous. While some difference in creep strength could be detected between samples from the depleted regions and those taken from undepleted regions, the effects were small, and much less than might be expected from the level of carbon difference present.

## 4 Carbon Diffusion Modelling and Detailed Analysis of Carbides

Following the work within Innogy described above, further studies were carried out by the Technical University of Graz under the auspices of the European Creep Collaborative Committee (Thematic Network “Weld-Creep”) Working Group 3.1. The main interest of the group was the application of TU Graz’s diffusion model to 9Cr-2Cr dissimilar metal welds. However, because of a lack of welds of this type with long term operating experience, the model was also applied to the 2CrMo-½CrMoV combination where ex-service samples obtained after long term operation were available.

The diffusion model was applied to the weld metal and parent pipe chemical compositions corresponding to the three welds shown in Fig. 7, with their respective operating histories [8]. The results for total carbon content on the parent sides of the welds showed excellent agreement in each case between the model prediction and the carbon by combustion measurements carried out independently. An example is shown in Fig. 9.

The modelling work also predicted the individual carbide types contributing to the carbon depletion. It was predicted that both carbon depletion in the ½CrMoV parent and carbon enrichment in the 2CrMo weld metal was the result of dissolution and growth, respectively, of the M23C6 type carbides. Significantly, the VC carbides were largely unaffected, with the amount present in the ½CrMoV parent persisting at an almost constant level up to the fusion line.  This is shown in Fig. 10.

In the second part of their work [9] TU Graz carried out a detailed electron microscopy study to identify which carbides were actually present in the samples. Excellent agreement was again found between prediction and observation.

## 5 Summary and Conclusions

Cracking in fully grain refined HAZ structure immediately adjacent to the fusion line has been found to occur on welds in ½CrMoV pipework systems operating at high temperature in the UK. Termed Type IIIa, the cracking has increased in significance as power plant has aged.

It has been shown that substantial carbon diffusion occurs during service in welds on ½CrMoV pipework systems operating at high temperature. The diffusion, resulting in the develoment of a band of carbon depletion and a band of carbon enrichment in the ½CrMoV parent and 2CrMo weld respectively, gives rise to a sharp mismatch in carbon level at the weld fusion line. The carbon mismatch, which increases with time, will inevitably produce an associated mismatch in creep strength either side of the fusion line. This appears to be the most likely explanation for the emergence of Type IIIa cracking at this location.

Although marked carbon loss has been measured in the parent adjacent to the fusion line in ex-service welds, it has not been possible to demonstrate a comparable loss of creep strength in the carbon depleted material. The electron microscope study carried out at the Technical University of Graz has provided an explanation for this anomaly, in that it has shown that the carbon diffusion is primarily affecting the coarser M23C6 type carbides while having limited affect on the finer VC carbides. It is the finer carbides which will be more likely to be controlling creep strength in the ½CrMoV pipe material. An increase in creep strength just within the weld metal may be the more significant contribution to the mismatch. There is no significant level of vanadium in this region and the carbon enriched layer here is associated with increased amounts of M23C6 carbides, the carbide type on which the 2CrMo weld metal creep strength is critically dependent.

The strength mismatch will continue to develop with time at service temperature, increasing the risk of Type IIIa crack initiation at this location. In contrast it can be argued that the Type IV zone, which enters service with low creep strength, is not likely to become significantly less strong with time. The implication is that Type IIIa cracks will become relatively more numerous as plant ages further.

6 Acknowledgements

This paper has been published with the permission of Innogy. The author would like to acknowledge the contribution of numerous colleagues, both inside and outside Innogy, during the course of the work described here.

7 References

[1] S J BRETT

In-Service Cracking Mechanisms Affecting 2CrMo Welds in ½CrMoV Steam Pipework Systems. Proceedings of IOM/IMechE Conference: Integrity of High-Temperature Welds, p3, Nottingham, November 3-4, 1998.

[2] S J BRETT & P A SMITH

Type IIIa Cracking at 2CrMo Welds in ½CrMoV Pipework. Proceedings of Baltica IV: International Conference on Plant Maintenance for Managing Life & Performance, Helsinki-Stockholm-Helsinki, September 7-9, 1998.

[3] H J SCHÜLLER, L HAGN and A WOITSCHECK

Cracking in the Weld Region of Shaped Components in Hot Steam Pipe Lines - Materials Investigations.

Der Machinenschaden 1974 47 p1.

[4]  S T KIMMINS and E L LONGLEY

Unpublished work carried out within National Power

[5] P A SMITH

Investigation into Fusion Boundary Carbon Diffusion in ½Cr½Mo¼V Weldments.

MSc Thesis, Cranfield University, September 1994.

[6] N ROBERTS

Carbon Diffusion in CrMoV Welds.

MRes Project 1998-1999, University of Wales, Swansea, Supervisors: J D Robson/B J Hulm.

[7] R HAYES

Effect of Carbon Depletion on the Creep Properties of CrMoV Steel.

MRes Project 1999-2000, University of Wales, Swansea, Supervisor: B J Hulm.

[8] E KOZESCHNIK, P PÖLT, S BRETT & B BUCHMAYR

Dissimilar 2.25Cr/9Cr and 2Cr/0.5CrMoV Steel Welds. Part 1: Characterisation of Weld Zone and Numerical Simulation. Science & Technology of Welding & Joining Vol. 7, No. 2, p63, 2002

[9] E KOZESCHNIK, P WARBICHLER, I LETOFSKY-PAPST,

S BRETT & B BUCHMAYR

Dissimilar 2.25Cr/9Cr and 2Cr/0.5CrMoV Steel Welds - Part 2: Identification of Precipitates. Science & Technology of Welding & Joining Vol. 7, No. 2, p69, 2002

Fig. 1.	Type IIIa cavitation and the initial stages of micro-cracking adjacent to the fusion line.

Fig. 2.	Type IIIa crack in a ½CrMoV plain butt weld.

Fig. 3.	The through-wall size distributions of Type IV and IIIa cracks found on coal-fired plant.

Fig. 4.	Relative Incidence of Type IV and IIIa Cracks  (Innogy 2001)

Fig. 5.	Comparison of carbon level in samples taken close to welds with samples taken remote form welds, and with analyses from test certificates.

Fig. 6.  Carbon distribution across the fusion line obtained by neutron microprobe (from Ref. 5). Sample aged for 884 hours at 642°C after welding.

Fig. 7.  Carbon profiles for three ex-service welds in ½CrMoV pipe.

Fig. 8.  Variation of carbon level (3mm from the fusion line) with hours in service (nominally at 568°C).

Fig. 9.  Comparison of  measured carbon level (WDX) with TU Graz model prediction after 180,000 hours service (from Ref. 8). The open squares are carbon by combustion measurements for the same weld.

Fig. 10. Predictions of individual carbide types for the weld shown in Fig. 9 (from Ref. 8).